## CIS Marking Scheme Import
38 Refrigeration and Air Conditioning
WorldSkills Standards Specification
Section | WSSS Marks | [6 empty] | WSSS Marks | Aspect Marks | Variation
1 | Work organization and management | [6 empty] | 10
2 | Communication and interpersonal skills | [6 empty] | 5
3 | Design refrigeration and air conditioning systems | [6 empty] | 15
4 | Installation and maintenance of refrigeration and air conditioning | [6 empty] | 30
5 | Commission refrigeration and air conditioning systems | [6 empty] | 20
6 | Fault finding refrigeration and air conditioning systems | [6 empty] | 20
Total Variation
Criteria
ID | Name | [8 empty] | Mark
A | Component Fabrication | [8 empty] | 12.5
B | Component and System Installation | [8 empty] | 20.6
C | Electrical Installation | [8 empty] | 14.1
D | Commissioning and Adjustment | [8 empty] | 17.1
E | Electrical Fault Find and Repair | [8 empty] | 10.5
F | Refrigeration Fault Find and Repair | [8 empty] | 9.8
G | Refrigerant Recovery and Control | [8 empty] | 8.5
H | Work Practices and Safety | [8 empty] | 6.9
I
Sub Criterion ID | Sub Criterion Name or Description | Day of Marking | Aspect Type M = Meas J = Judg | Aspect - Description | Judg Score | Extra Aspect Description (Meas or Judg) OR Judgement Score Description (Judg only) | Requirement (Measurement Only) | WSSS Section | Calculation Row (Export only) | Max Mark | Criterion A | Total Mark
A1 | Module A - Ice Tank Coil Fabrication | 1
|  |  | M | Dimension A |  | Does it meet the drawing specification? | 240mm +/- 2mm | 2 |  | 0.4
|  |  | M | Dimension B |  | Does it meet the drawing specification? | 352mm +/- 2mm | 2 |  | 0.25
|  |  | M | Dimension C1 |  | Does it meet the drawing specification? | 40mm +/- 2mm | 2 |  | 0.35
|  |  | M | Dimension C2 |  | Does it meet the drawing specification? | 40mm +/- 2mm | 4 |  | 0.25
|  |  | M | Dimension D |  | Does it meet the drawing specification? | 200mm +/- 2mm | 2 |  | 0.25
|  |  | M | Dimension E1 |  | Does it meet the drawing specification? | 50mm +/- 2mm | 4 |  | 0.25
|  |  | M | Dimension E2 |  | Does it meet the drawing specification? | 50mm +/- 2mm | 4 |  | 0.25
|  |  | M | U-bend diameter |  | Are they the correct diameter? | 88mm +/-2mm | 4 |  | 0.25
|  |  | M | U-bend arc |  | Are the bent tubes parallel? | Tubes parallel +/- 2mm measured over a distance of 180mm | 4 |  | 0.3
|  |  | M | Right angle bends |  | Are they at correct angle? | 90 Deg +/- 2 Deg | 4 |  | 0.3
|  |  | M | Tube straightness |  | Are the required straight tubes straight when put against a straight edge? | Straight +/- 2mm over 300mm | 4 |  | 0.3
|  |  | M | Pipe clamps |  | Are they securely fastened to the coil? | Yes | 4 |  | 0.3
|  |  | M | Dry Nitrogen |  | Was Dry Nitrogen correctly used during brazing of the support tubes to the coil? | Yes | 4 |  | 0.4
|  |  | J | Cross tube brazed joints |  |  |  | 3 |  | 0.3
[5 empty] | 0 | Performance is below industry standard:- Dry nitrogen not used, or incorrect, not a complete ring or too much (blobs) brazing alloy used, or brazing alloy not melted into joint, or metal damaged/burnt or flux residue.
[5 empty] | 1 | Performance meets industry standards – Dry nitrogen used, correct brazing alloy used and its brazing alloy ring is complete but not even or insufficient or more than 2mm excess, with no metal damage, no flux residue or component scorching, but some over-heating of alloy (bubbles)
[5 empty] | 2 | Performance meets industry standards and surpasses that standard to some extent - Dry nitrogen used, correct brazing alloy used and its brazing alloy ring is complete but not even or insufficient or more than 2mm excess, with no metal damage, no flux residue or component scorching and no over-heating of alloy.
[5 empty] | 3 | Excellent or outstanding performance relative to industry expectation - Dry nitrogen used, correct brazing alloy used and its brazing ring is complete, even, smooth and sufficient with less than 2mm excess with no metal damage, over-heating or flux residue.
|  |  | J | U-bends |  |  |  | 4 |  | 0.25
[5 empty] | 0 | Performance below industry standards - Large kinks, grooves or scratches on pipe, bend angle not correct (180 Deg +/- 5 Deg), diameter of the pipe reduced, more than three blemishes (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 1 | Performance meets industry standards - Small kinks, grooves or scratches on pipe, bend angle correct (180 Deg +/- 5 Deg), diameter of the pipe slightly reduced, two blemishes (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 2 | Performance meets industry standards and surpasses that standard to some extent - Minor small kinks, grooves or scratches on pipe, but defects will not affect operation, bend angle correct (180 Deg +/- 5 Deg), diameter of the pipe correct, one blemish (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 3 | Excellent or outstanding performance relative to industry expectation - No kinks, no grooves or no scratches on pipe, bend angle correct (180 Deg +/- 2 Deg), diameter of the pipe full and correct (marks or scratches caused by the bender’s correct use not included)
|  |  | J | Right angle bends |  |  |  | 4 |  | 0.25
[5 empty] | 0 | Performance below industry standards - Large kinks, grooves or scratches on pipe, bend angle not correct (90 Deg +/- 5 Deg diameter of the pipe reduced, more than three blemishes (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 1 | Performance meets industry standards - Small kinks, grooves or scratches on pipe, bend angle correct (90 Deg +/- 5 Deg), diameter of the pipe slightly reduced, two blemishes (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 2 | Performance meets industry standards and surpasses that standard to some extent - Minor small kinks, grooves or scratches on pipe, but defects will not affect operation, bend angle correct (90 Deg +/- 5 Deg), diameter of the pipe correct, one blemish (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 3 | Excellent or outstanding performance relative to industry expectation - No kinks, no grooves or no scratches on pipe, bend angle correct (90 Deg +/- 2 Deg), diameter of the pipe full and correct (marks or scratches caused by the bender’s correct use not included)
|  |  | J | Overall coil |  |  |  | 4 |  | 0.25
[5 empty] | 0 | Performance below industry standards - Coil not complete, large kinks, grooves, scratches on pipe, large dobs of solder or pipe not straight or parallel to each other, legs (stands) not vertical or secure
[5 empty] | 1 | Performance meets industry standards - Coil complete, but may have some small kinks, grooves, scratches or dobs of solder on pipe and pipe mostly straight and parallel to each other, legs (stands) mostly vertical and secure ( two or more are not)
[5 empty] | 2 | Performance meets industry standards and surpasses that standard to some extent - Coil complete, could have some minor kinks, grooves, scratches on pipe, neat solder and pipes straight and parallel to each other, legs(stands) vertical and secure except for one leg, - defects will not affect operation
[5 empty] | 3 | Excellent or outstanding performance relative to industry expectation - Coil complete, no kinks, no grooves, no scratches on pipe, all neat solder and all pipes straight and parallel to each other, all legs (stands) vertical and secure
A2 | Module A - Heat Recovery Coil Fabrication | 1
|  |  | M | Dimension A |  | Does it meet the drawing specification? | 250mm +/- 2mm | 2 |  | 0.4
|  |  | M | Dimension B |  | Does it meet the drawing specification? | 352mm +/- 2mm | 2 |  | 0.4
|  |  | M | Dimension C |  | Does it meet the drawing specification? | 40mm +/- 2mm | 2 |  | 0.4
|  |  | M | Dimension D |  | Does it meet the drawing specification? | 300mm +/- 2mm | 2 |  | 0.4
|  |  | M | Dimension E |  | Does it meet the drawing specification? | 88mm +/- 2mm | 4 |  | 0.4
|  |  | M | Dimension F |  | Does it meet the drawing specification? | 90mm +/- 2mm | 2 |  | 0.6
|  |  | M | Dimension G |  | Does it meet the drawing specification? | 175mm +/- 2mm | 4 |  | 0.3
|  |  | M | U-bend diameter |  | Are they the correct diameter? | 88mm +/-2mm | 4 |  | 0.4
|  |  | M | U-bend arc |  | Are the bent tubes parallel? | Tubes parallel +/- 2mm measured over a distance of 180mm | 4 |  | 0.4
|  |  | M | Right angle bends |  | Are they at correct angle? | 90 Deg +/- 2 Deg | 4 |  | 0.4
|  |  | M | Tube straightness |  | Are the required straight tubes straight when put against a straight edge? | Straight +/- 2mm over 300mm | 4 |  | 0.4
|  |  | M | Dry Nitrogen |  | Was Dry Nitrogen correctly used during brazing of the support tubes to the coil? | Yes | 4 |  | 0.4
|  |  | J | Support tube brazed joints |  |  |  | 3 |  | 0.3
[5 empty] | 0 | Performance is below industry standard:- Dry nitrogen not used, or incorrect, not a complete ring or too much (blobs) brazing alloy used, or brazing alloy not melted into joint, or metal damaged/burnt or flux residue.
[5 empty] | 1 | Performance meets industry standards – Dry nitrogen used, correct brazing alloy used and its brazing alloy ring is complete but not even or insufficient or more than 2mm excess, with no metal damage, no flux residue or component scorching, but some over-heating of alloy (bubbles)
[5 empty] | 2 | Performance meets industry standards and surpasses that standard to some extent - Dry nitrogen used, correct brazing alloy used and its brazing alloy ring is complete but not even or insufficient or more than 2mm excess, with no metal damage, no flux residue or component scorching and no over-heating of alloy.
[5 empty] | 3 | Excellent or outstanding performance relative to industry expectation - Dry nitrogen used, correct brazing alloy used and its brazing ring is complete, even, smooth and sufficient with less than 2mm excess with no metal damage, over-heating or flux residue.
|  |  | J | U-bends |  |  |  | 4 |  | 0.4
[5 empty] | 0 | Performance below industry standards - Large kinks, grooves or scratches on pipe, bend angle not correct (180 Deg +/- 2 Deg), diameter of the pipe reduced, more than three blemishes (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 1 | Performance meets industry standards - Small kinks, grooves or scratches on pipe, bend angle correct (180 Deg +/- 2 Deg), diameter of the pipe slightly reduced, two blemishes (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 2 | Performance meets industry standards and surpasses that standard to some extent - Minor small kinks, grooves or scratches on pipe, but defects will not affect operation, bend angle correct (180 Deg +/- 2 Deg), diameter of the pipe correct, one blemish (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 3 | Excellent or outstanding performance relative to industry expectation - No kinks, no grooves or no scratches on pipe, bend angle correct (180 Deg +/- 2 Deg), diameter of the pipe full and correct (marks or scratches caused by the bender’s correct use not included)
|  |  | J | Right angle bends |  |  |  | 4 |  | 0.4
[5 empty] | 0 | Performance below industry standards - Large kinks, grooves or scratches on pipe, bend angle not correct (90 Deg +/- 5 Deg), diameter of the pipe reduced, more than three blemishes (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 1 | Performance meets industry standards - Small kinks, grooves or scratches on pipe, bend angle correct (90 Deg +/- 5 Deg), diameter of the pipe slightly reduced, two blemishes (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 2 | Performance meets industry standards and surpasses that standard to some extent - Minor small kinks, grooves or scratches on pipe, but defects will not affect operation, bend angle correct (90 Deg +/- 5 Deg), diameter of the pipe correct, one blemish (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 3 | Excellent or outstanding performance relative to industry expectation - No kinks, no grooves or no scratches on pipe, bend angle correct (90 Deg +/- 5 Deg), diameter of the pipe full and correct (marks or scratches caused by the bender’s correct use not included)
|  |  | J | Overall coil |  |  |  | 4 |  | 0.4
[5 empty] | 0 | Performance below industry standards - Coil not complete, large kinks, grooves, scratches on pipe, large dobs of solder or pipe not straight or parallel to each other, legs (stands) not vertical or secure
[5 empty] | 1 | Performance meets industry standards - Coil complete, but may have some small kinks, grooves, scratches or dobs of solder on pipe and pipe mostly straight and parallel to each other, legs (stands) mostly vertical and secure ( two or more are not)
[5 empty] | 2 | Performance meets industry standards and surpasses that standard to some extent - Coil complete, could have some minor kinks, grooves, scratches on pipe, neat solder and pipes straight and parallel to each other, legs(stands) vertical and secure except for one leg, - defects will not affect operation
[5 empty] | 3 | Excellent or outstanding performance relative to industry expectation - Coil complete, no kinks, no grooves, no scratches on pipe, all neat solder and all pipes straight and parallel to each other, all legs (stands) vertical and secure
A3 | Module A - Work organisation and management | 1
|  |  | M | Fabrication time |  | Were both coils completed in 150 minutes? | Yes/No | 1 |  | 0.4
|  |  | M | Fabrication completion |  | Were both coils completed in 180 minutes? | Yes/No | 1 |  | 0.4
|  |  | M | Efficient use of material - sustainability |  | Was NO additional copper tube given to the competitor? | Yes/No | 1 |  | 0.4
Sub Criterion ID | Sub Criterion Name or Description | Day of Marking | Aspect Type M = Meas J = Judg | Aspect - Description | Judg Score | Extra Aspect Description (Meas or Judg) OR Judgement Score Description (Judg only) | Requirement (Measurement Only) | WSSS Section | Calculation Row (Export only) | Max Mark | Criterion B | Total Mark
B1 | Module B - Major Component installation | 1
|  |  | M | Compressor installation |  | Is it installed in specified location using mounting kit and securely fixed? | Refer drawing 38.07, +/- 2mm, 3 mounting points per manufactures instructions | 4 |  | 0.2
|  |  | M | Air cooled condenser installation |  | Is it installed in specified location and securely fixed? | Refer drawing 38.07, +/- 2mm | 4 |  | 0.2
|  |  | M | Liquid receiver installation |  | Is it installed in specified location and securely fixed? | Refer drawing 38.07, +/- 2mm | 4 |  | 0.2
|  |  | M | Suction accumulator installation |  | Is it installed in specified location and securely fixed? | Refer drawing 38.07, +/- 2mm | 4 |  | 0.2
|  |  | M | Electrical control box installation |  | Is it installed in specified location and securely fixed? | Refer drawing 38.07, +/- 2mm | 4 |  | 0.2
|  |  | M | Pressure control installation |  | Are they installed in specified location, level and securely fixed? | Refer drawing 38.07, +/- 2mm | 4 |  | 0.2
B2 | Module B - Refrigerant Controls Installation | 3
|  |  | M | Thermostatic expansion valve installation |  | Is it installed in the correct location in system, with correct flow and as per manufacturer instructions? | Refer drawing 38.001 and manufacturers installation instructions | 3 |  | 0.2
|  |  | M | Hot gas bypass valve |  | Is it installed in the correct location in system, with correct flow and as per manufacturer instructions? | Refer drawing 38.001 and manufacturers installation instructions | 3 |  | 0.2
|  |  | M | Crankcase pressure regulator |  | Is it installed in the correct location in system, with correct flow and as per manufacturer instructions? | Refer drawing 38.001 and manufacturers installation instructions | 3 |  | 0.2
|  |  | M | Solenoid valves |  | Are they installed in the correct location in system, with correct flow and as per manufacturer instructions? | Refer drawing 38.001 and manufacturers installation instructions | 3 |  | 0.2
|  |  | M | Ball valves |  | Are they installed in the correct location in system, with correct flow and as per manufacturer instructions? | Are they installed in the correct location in system, with correct flow and as per manufacturer instructions | 3 |  | 0.2
|  |  | M | Check valve |  | Is it installed in the correct location in system, with correct flow and as per manufacturer instructions? | Refer drawing 38.001 and manufacturers installation instructions | 3 |  | 0.2
|  |  | M | Pressure relief valve |  | Is it installed in the correct location in system, with correct flow and as per manufacturer instructions? | Refer drawing 38.001 and manufacturers installation instructions | 3 |  | 0.2
|  |  | M | Liquid line filter dryer |  | Is it installed in the correct location in system, with correct flow and as per manufacturer instructions? | Refer drawing 38.001 and manufacturers installation instructions | 3 |  | 0.2
|  |  | M | Sight glass |  | Is it installed in the correct location in system, with correct flow and as per manufacturer instructions? | Refer drawing 38.001 and manufacturers installation instructions | 3 |  | 0.2
|  |  | M | Pressure controls |  | Are the pressure controls piped as per specifications? | Refer drawing 38.001 and manufacturers installation instructions | 3 |  | 0.2
|  |  | M | Pressure gauges and their hand valves |  | Are they installed in the correct location, secure and with correct flow? | Refer drawing 38.07, +/- 2mm | 3 |  | 0.2
B3 | Module B - Low Pressure Vapour Lines | 3
|  |  | M | Horizontal and vertical pipework |  | Are all the pipes installed in vertical and horizontal planes and are the horizontal and vertical pipes straight? | Within deviation lines on spirit level | 3 |  | 0.4
|  |  | M | Pipework bends |  | Are all the bends an appropriate radius and angle with no kinks? | Yes/No | 3 |  | 0.4
|  |  | M | Pipework installation |  | Is the pipework installed so that it does not rub on any components? e.g. fan blades, other pipes, valves, etc. | Yes/No | 3 |  | 0.4
|  |  | M | Pipework fastenings |  | Is the pipework securely fastened using provided pipe clamps? | Yes/No | 4 |  | 0.4
|  |  | M | Pipework brazing procedure |  | Was dry Nitrogen used correctly during all pipework brazing to prevent oxidisation? | Yes/No | 4 |  | 0.5
|  |  | M | Pipework insulation |  | Is all of the relevant pipework insulated appropriately? | Yes/No | 4 |  | 0.4
|  |  | J | Brazed joint #1 (copper to copper) |  |  |  | 3 |  | 0.3
[5 empty] | 0 | Performance below industry standards - Joint leaks under pressure, or dry nitrogen not used, or incorrect, not a complete ring or too much (blobs) brazing alloy used, or brazing alloy not melted into joint, or metal damaged/burnt or flux residue.
[5 empty] | 1 | Performance meets industry standards – Does not leak, dry nitrogen used, correct brazing alloy used and its brazing alloy ring is complete but not even or insufficient or more than 2mm excess, with no metal damage, no flux residue or component scorching, but some over-heating of alloy (bubbles)
[5 empty] | 2 | Performance meets industry standards and surpasses that standard to some extent - Does not leak, dry nitrogen used, correct brazing alloy used and its brazing alloy ring is complete but not even or insufficient or more than 2mm excess, with no metal damage, no flux residue or component scorching and no over-heating of alloy.
[5 empty] | 3 | Excellent or outstanding performance relative to industry expectation - Joint does not leak under pressure, dry nitrogen used, correct brazing alloy used and its brazing ring is complete, even, smooth and sufficient with less than 2mm excess with no metal damage, over-heating or flux residue
|  |  | J | Brazed joint on compressor's suction service valve |  |  |  | 3 |  | 0.3
[5 empty] | 0 | Performance below industry standards - Joint leaks under pressure, or dry nitrogen not used, or incorrect, not a complete ring or too much (blobs) brazing alloy used, or brazing alloy not melted into joint, or metal damaged/burnt or flux residue.
[5 empty] | 1 | Performance meets industry standards – Does not leak, dry nitrogen used, correct brazing alloy used and its brazing alloy ring is complete but not even or insufficient or more than 2mm excess, with no metal damage, no flux residue or component scorching, but some over-heating of alloy (bubbles)
[5 empty] | 2 | Performance meets industry standards and surpasses that standard to some extent - Does not leak, dry nitrogen used, correct brazing alloy used and its brazing alloy ring is complete but not even or insufficient or more than 2mm excess, with no metal damage, no flux residue or component scorching and no over-heating of alloy.
[5 empty] | 3 | Excellent or outstanding performance relative to industry expectation - Joint does not leak under pressure, dry nitrogen used, correct brazing alloy used and its brazing ring is complete, even, smooth and sufficient with less than 2mm excess with no metal damage, over-heating or flux residue
|  |  | J | Right angle bends |  |  |  | 4 |  | 0.4
[5 empty] | 0 | Performance below industry standards - Large kinks, grooves or scratches on pipe, bend angle not correct (90 Deg +/- 5 Deg), diameter of the pipe reduced, more than three blemishes (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 1 | Performance meets industry standards - Small kinks, grooves or scratches on pipe, bend angle correct (90 Deg +/- 5 Deg), diameter of the pipe slightly reduced, two blemishes (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 2 | Performance meets industry standards and surpasses that standard to some extent - Minor small kinks, grooves or scratches on pipe, but defects will not affect operation, bend angle correct (90 Deg +/- 5 Deg), diameter of the pipe correct, one blemish (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 3 | Excellent or outstanding performance relative to industry expectation - No kinks, no grooves or no scratches on pipe, bend angle correct (90 Deg +/- 5 Deg), diameter of the pipe full and correct (marks or scratches caused by the bender’s correct use not included)
B4 | Module B - High Pressure Liquid Line | 3
|  |  | M | Horizontal and vertical pipework |  | Are all the pipes installed in vertical and horizontal planes and are the horizontal and vertical pipes straight? | Within deviation lines on spirit level | 3 |  | 0.4
|  |  | M | Pipework bends |  | Are all the bends an appropriate radius and angle with no kinks? | Yes/No | 3 |  | 0.3
|  |  | M | Pipework layout |  | Are the pipes set out so that they don't cross each other? | Yes/No | 3 |  | 0.3
|  |  | M | Pipework installation |  | Is the pipework installed so that it does not rub on any components? e.g. fan blades, other tubes, valves, etc. | Yes/No | 3 |  | 0.3
|  |  | M | Pipework fastenings |  | Is the pipework securely fastened using provided pipe clamps? | Yes/No | 4 |  | 0.3
|  |  | M | Pipework brazing procedure |  | Was dry Nitrogen used correctly during all pipework brazing to prevent oxidisation? | Yes/No | 4 |  | 0.5
|  |  | J | Brazed joint #2 is acceptable (copper to copper) |  |  |  | 3 |  | 0.3
[5 empty] | 0 | Performance below industry standards - Joint leaks under pressure, or dry nitrogen not used, or incorrect, not a complete ring or too much (blobs) brazing alloy used, or brazing alloy not melted into joint, or metal damaged/burnt or flux residue.
[5 empty] | 1 | Performance meets industry standards – Does not leak, dry nitrogen used, correct brazing alloy used and its brazing alloy ring is complete but not even or insufficient or more than 2mm excess, with no metal damage, no flux residue or component scorching, but some over-heating of alloy (bubbles)
[5 empty] | 2 | Performance meets industry standards and surpasses that standard to some extent - Does not leak, dry nitrogen used, correct brazing alloy used and its brazing alloy ring is complete but not even or insufficient or more than 2mm excess, with no metal damage, no flux residue or component scorching and no over-heating of alloy.
[5 empty] | 3 | Excellent or outstanding performance relative to industry expectation - Joint does not leak under pressure, dry nitrogen used, correct brazing alloy used and its brazing ring is complete, even, smooth and sufficient with less than 2mm excess with no metal damage, over-heating or flux residue
|  |  | J | Brazed joint on liquid receiver inlet |  |  |  | 3 |  | 0.3
[5 empty] | 0 | Performance below industry standards - Joint leaks under pressure, or dry nitrogen not used, or incorrect, not a complete ring or too much (blobs) brazing alloy used, or brazing alloy not melted into joint, or metal damaged/burnt or flux residue.
[5 empty] | 1 | Performance meets industry standards – Does not leak, dry nitrogen used, correct brazing alloy used and its brazing alloy ring is complete but not even or insufficient or more than 2mm excess, with no metal damage, no flux residue or component scorching, but some over-heating of alloy (bubbles)
[5 empty] | 2 | Performance meets industry standards and surpasses that standard to some extent - Does not leak, dry nitrogen used, correct brazing alloy used and its brazing alloy ring is complete but not even or insufficient or more than 2mm excess, with no metal damage, no flux residue or component scorching and no over-heating of alloy.
[5 empty] | 3 | Excellent or outstanding performance relative to industry expectation - Joint does not leak under pressure, dry nitrogen used, correct brazing alloy used and its brazing ring is complete, even, smooth and sufficient with less than 2mm excess with no metal damage, over-heating or flux residue
|  |  | J | Right angle bends |  |  |  | 4 |  | 0.4
[5 empty] | 0 | Performance below industry standards - Large kinks, grooves or scratches on pipe, bend angle not correct (90 Deg +/- 5 Deg), diameter of the pipe reduced, more than three blemishes (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 1 | Performance meets industry standards - Small kinks, grooves or scratches on pipe, bend angle correct (90 Deg +/- 5 Deg), diameter of the pipe slightly reduced, two blemishes (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 2 | Performance meets industry standards and surpasses that standard to some extent - Minor small kinks, grooves or scratches on pipe, but defects will not affect operation, bend angle correct (90 Deg +/- 5 Deg), diameter of the pipe correct, one blemish (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 3 | Excellent or outstanding performance relative to industry expectation - No kinks, no grooves or no scratches on pipe, bend angle correct (90 Deg +/- 5 Deg), diameter of the pipe full and correct (marks or scratches caused by the bender’s correct use not included)
B5 | Module B - High Pressure Discharge Line | 3
|  |  | M | Horizontal and vertical pipework |  | Are all the pipes installed in vertical and horizontal planes and are the horizontal and vertical pipes straight? | Within deviation lines on spirit level | 3 |  | 0.4
|  |  | M | Pipework bends |  | Are all the bends an appropriate radius and angle with no kinks? | Yes/No | 3 |  | 0.4
|  |  | M | Pipework installation |  | Is the pipework installed so that it does not rub on any components? e.g. fan blades, other tubes, valves, etc. | Yes/No | 3 |  | 0.4
|  |  | M | Pipework fastenings |  | Is the pipework securely fastened using provided pipe clamps? | Yes/No | 4 |  | 0.4
|  |  | M | Pipework brazing procedure |  | Was dry Nitrogen used correctly during all pipework brazing to prevent oxidisation? | Yes/No | 4 |  | 0.5
|  |  | J | Brazed joint #3 is acceptable (copper to copper) |  |  |  | 3 |  | 0.3
[5 empty] | 0 | Performance below industry standards - Joint leaks under pressure, or dry nitrogen not used, or incorrect, not a complete ring or too much (blobs) brazing alloy used, or brazing alloy not melted into joint, or metal damaged/burnt or flux residue.
[5 empty] | 1 | Performance meets industry standards – Does not leak, dry nitrogen used, correct brazing alloy used and its brazing alloy ring is complete but not even or insufficient or more than 2mm excess, with no metal damage, no flux residue or component scorching, but some over-heating of alloy (bubbles)
[5 empty] | 2 | Performance meets industry standards and surpasses that standard to some extent - Does not leak, dry nitrogen used, correct brazing alloy used and its brazing alloy ring is complete but not even or insufficient or more than 2mm excess, with no metal damage, no flux residue or component scorching and no over-heating of alloy.
[5 empty] | 3 | Excellent or outstanding performance relative to industry expectation - Joint does not leak under pressure, dry nitrogen used, correct brazing alloy used and its brazing ring is complete, even, smooth and sufficient with less than 2mm excess with no metal damage, over-heating or flux residue
|  |  | J | Brazed pipe joint on Pressure relief valve brass union |  |  |  | 3 |  | 0.3
[5 empty] | 0 | Performance below industry standards - Joint leaks under pressure, or dry nitrogen not used, or incorrect, not a complete ring or too much (blobs) brazing alloy used, or brazing alloy not melted into joint, or metal damaged/burnt or flux residue.
[5 empty] | 1 | Performance meets industry standards – Does not leak, dry nitrogen used, correct brazing alloy used and its brazing alloy ring is complete but not even or insufficient or more than 2mm excess, with no metal damage, no flux residue or component scorching, but some over-heating of alloy (bubbles)
[5 empty] | 2 | Performance meets industry standards and surpasses that standard to some extent - Does not leak, dry nitrogen used, correct brazing alloy used and its brazing alloy ring is complete but not even or insufficient or more than 2mm excess, with no metal damage, no flux residue or component scorching and no over-heating of alloy.
[5 empty] | 3 | Excellent or outstanding performance relative to industry expectation - Joint does not leak under pressure, dry nitrogen used, correct brazing alloy used and its brazing ring is complete, even, smooth and sufficient with less than 2mm excess with no metal damage, over-heating or flux residue
|  |  | J | Right angle bends |  |  |  | 4 |  | 0.4
[5 empty] | 0 | Performance below industry standards - Large kinks, grooves or scratches on pipe, bend angle not correct (90 Deg +/- 5 Deg), diameter of the pipe reduced, more than three blemishes (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 1 | Performance meets industry standards - Small kinks, grooves or scratches on pipe, bend angle correct (90 Deg +/- 5 Deg), diameter of the pipe slightly reduced, two blemishes (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 2 | Performance meets industry standards and surpasses that standard to some extent - Minor small kinks, grooves or scratches on pipe, but defects will not affect operation, bend angle correct (90 Deg +/- 5 Deg), diameter of the pipe correct, one blemish (marks or scratches caused by the bender’s correct use not included)
[5 empty] | 3 | Excellent or outstanding performance relative to industry expectation - No kinks, no grooves or no scratches on pipe, bend angle correct (90 Deg +/- 5 Deg), diameter of the pipe full and correct (marks or scratches caused by the bender’s correct use not included)
B6 | Module B - Pressure Test | 3
|  |  | M | Test pressure |  | Did the test pressure during all attempts meet required standards and specifications? | Refer standards section 4 and test project 55 DegC = 1,390 kPa +/- 35 kPa or 202 PSI +/- 5 PSI | 4 |  | 0.5
|  |  | M | System valves |  | Were all the appropriate valves opened to ensure pressure testing of the entire system? | Check all valves in system | 4 |  | 0.3
|  |  | M | Gauges fitted |  | Were the gauges and gauge lines correctly fitted to the system? | Refer standards section 4 | 4 |  | 0.3
|  |  | M | Dry Nitrogen |  | Was dry Nitrogen safely added to the system to the required test pressure? | Refer standards section 4 and test project instructions | 4 |  | 0.3
|  |  | M | Leak test |  | Was the system was leak tested while under pressure? | Soapy water solution, Refer standards section 4 | 4 |  | 0.5
|  |  | M | First leak test |  | Were no leaks detected on FIRST pressure test attempt? | Test project instructions | 4 |  | 1
|  |  | M | Final leak test |  | Did the system hold the test pressure for required standing time (15 minutes) after any leaks repaired? | Refer standards section 4, and test project | 4 |  | 1
|  |  | M | Pressure release |  | Was the dry Nitrogen safely released from system at completion of pressure test? | Refer standards section 4 | 4 |  | 0.3
B7 | Module B - Evacuation | 3
|  |  | M | System valves |  | Were the appropriate valves opened to ensure evacuation of the entire system? |  | 4 |  | 0.3
|  |  | M | Vacuum pump |  | Was the vacuum pump connected to the system correctly? | Yes/No | 4 |  | 0.3
|  |  | M | Vacuum gauge |  | Was the vacuum gauge installed so it could be isolated from the vacuum pump and still measure the system's pressure? | Yes/No | 4 |  | 0.3
|  |  | M | Vacuum pressure reached |  | Did the system reach the required vacuum level on the first attempt? | At least 1000 microns | 4 |  | 0.4
|  |  | M | Vacuum holding pressure |  | Did the vacuum hold when isolated from the vacuum pump for 10 minutes after the FIRST attempt? | Refer standards section 4 and test project. Not rise more than 500 microns in 10 minutes | 4 |  | 0.5
|  |  | M | Final vacuum pressures |  | Did the system reach and hold the required vacuum on the FINAL attempt? | Refer standards section 4, - and test project | 4 |  | 1.5
Sub Criterion ID | Sub Criterion Name or Description | Day of Marking | Aspect Type M = Meas J = Judg | Aspect - Description | Judg Score | Extra Aspect Description (Meas or Judg) OR Judgement Score Description (Judg only) | Requirement (Measurement Only) | WSSS Section | Calculation Row (Export only) | Max Mark | Criterion C | Total Mark
C1 | Module B - Connect the Electrical Circuit | 4
|  |  | M | All electrical wiring |  | Is all wiring installed and connected per supplied wiring diagram? | Refer 38.02, 38.03, 38.04. 38.06 | 2 |  | 0.5
|  |  | M | Electrical supply plug |  | Is the electrical supply wired correctly on supplied plug? | Yes/no | 4 |  | 0.5
|  |  | M | Control board electrical supply |  | Is the 220V supply wired to correct terminals and correctly terminated? | Refer 38.02, 38.03, 38.04. 38.06 | 4 |  | 0.5
|  |  | M | Compressor wiring |  | Is the compressor wired to correct terminals in control board and starting kit, and correctly terminated? | Refer 38.02, 38.03, 38.04. 38.06 | 4 |  | 0.5
|  |  | M | Condenser fan motor |  | Is the wiring connected and terminated correctly at the motor and the control board? | Refer 38.02, 38.03, 38.04. 38.06 | 4 |  | 0.5
|  |  | M | Solenoid valve - normally open |  | Is the wiring connected and terminated correctly at the valve and the control board? | Refer 38.02, 38.03, 38.04. 38.06 | 4 |  | 0.5
|  |  | M | Solenoid valve - normally closed |  | Is the wiring connected and terminated correctly at the valve and the control board? | Refer 38.02, 38.03, 38.04. 38.06 | 4 |  | 0.5
|  |  | M | Dual pressure control |  | Is the wiring connected and terminated correctly at the DPC and the control board? | Refer 38.02, 38.03, 38.04. 38.06 | 4 |  | 0.5
|  |  | M | High pressure control |  | Is the wiring connected and terminated correctly at the HPC and the control board? | Refer 38.02, 38.03, 38.04. 38.06 | 4 |  | 0.5
|  |  | M | Cable duct (channel) |  | Is it vertically and horizontally levelled and securely fastened? | Within deviation lines on spirit level | 3 |  | 0.5
|  |  | M | Flexible cables secured |  | Are all flexible cables not in duct saddled (fixed) and secured separate to piping? | Secured at least every 400mm | 4 |  | 0.3
|  |  | M | Flexible cable condition |  | Are the installed cables not be crushed or damaged by piping or other components? | Yes/No | 3 |  | 0.3
|  |  | M | Flexible cable protection |  | Are all installed cables and wires adequately protected? | Conduit or double insulated flexible cable | 3 |  | 0.3
|  |  | M | Cable and duct locations |  | Are all cables and duct installed within the boundaries of the supplied unit frame? | Front or rear of frame | 3 |  | 0.5
C2 | Module B - Connect the Electronic Controls (Thermostats) | 4
|  |  | M | Ice temperature probe wiring |  | Is the temperature probe wired and terminated correctly? | Refer 38.02, 38.03, 38.04. 38.06 | 4 |  | 0.2
|  |  | M | Ice temperature probe installation |  | Is the temperature probe securely installed in suitable location? | Refer 38.02, 38.03, 38.04. 38.06 | 3 |  | 0.2
|  |  | M | Heat recovery temperature probe wiring |  | Is the temperature probe wired and terminated correctly? | Refer 38.02, 38.03, 38.04. 38.06 | 4 |  | 0.2
|  |  | M | Heat recovery temperature probe installation |  | Is the temperature probe securely installed in suitable location? | Refer 38.02, 38.03, 38.04. 38.06 | 3 |  | 0.2
C3 | Module B - Electrical Testing | 4
|  |  | M | Supply voltage to earth |  | Was the supply voltage measured and confirmed correct? | 220v a.c +/- 10v | 5 |  | 0.2
|  |  | M | Supply votlage to neutral |  | Was the supply voltage measured and confirmed correct? | 220v a.c +/- 10v | 5 |  | 0.2
|  |  | M | Earth continuity to control board |  | Was the earth continuity of the power supply to the control board tested and found to meet requirements? | Less than 1ohm | 5 |  | 0.2
|  |  | M | Earth continuity to compressor, fan motor and solenoid valves |  | Was the earth continuity of the power supply to the compressor, fan motor and solenoid valves tested and found to meet requirements? | Less than 1ohm | 5 |  | 0.2
|  |  | M | Supply continuity to control board |  | Was the earth continuity of the power supply to the compressor, fan motor and solenoid valves tested and found to meet requirements? | Less than 1ohm | 5 |  | 0.5
|  |  | M | Earth leakage |  | Was the installation tested for earth leakage using a Megohm-meter prior to energising and found to be acceptable? | Infinity | 6 |  | 0.6
|  |  | M | Short circuits |  | Was the installation tested for shorts between active and neutral prior to energising and found to be acceptable? | Greater than 100ohm | 6 |  | 0.6
|  |  | M | Electrical testing faults |  | Were No electrical faults found during circuit testing? | Yes/No | 6 |  | 1.2
|  |  | M | Energising circuit |  | Was the circuit energised safely the first time without blowing fuses/circuit breakers/etc? | Yes/No | 5 |  | 1.2
|  |  | M | Circuit's first operation |  | Did the circuit work safely and correctly the first time it was operated without wiring modifications? | Refer 38.02, 38.03, 38.04. 38.06 | 5 |  | 1
|  |  | M | Circuit's final operation |  | Did the circuit work safely and correctly after any necessary modifications were completed? | Refer 38.02, 38.03, 38.04. 38.06 | 5 |  | 1
Sub Criterion ID | Sub Criterion Name or Description | Day of Marking | Aspect Type M = Meas J = Judg | Aspect - Description | Judg Score | Extra Aspect Description (Meas or Judg) OR Judgement Score Description (Judg only) | Requirement (Measurement Only) | WSSS Section | Calculation Row (Export only) | Max Mark | Criterion D | Total Mark
D1 | Module B - Charge with Refrigerant | 4
|  |  | M | Refrigerant service manifold |  | Was the refrigerant service manifold correctly connected to the refrigeration system and refrigerant cylinder to charge the system with refrigerant? | Yes/No | 5 |  | 0.4
|  |  | M | Refrigeration system's valves |  | Were all the refrigeration system's valves in correct position to charge the system with refrigerant? | Yes/No | 5 |  | 0.4
|  |  | M | Liquid refrigerant |  | Was liquid refrigerant added to the liquid line only (not suction)? | Yes/No | 5 |  | 0.5
|  |  | M | Adding liquid refrigerant |  | Was liquid refrigerant added to the system using correct method with no or minimal loss of refrigerant to the atmosphere? | R134a liquid charge | 5 |  | 0.5
|  |  | M | Liquid refrigerant quantity |  | Was the initial quantity of refrigerant added to the system as specified? | 1/5kg +/- 100g | 5 |  | 0.5
|  |  | M | Adding vapour refrigerant |  | Was vapour refrigerant added to the system using correct method with no or minimal loss of refrigerant to the atmosphere? | R134a vapour charge | 5 |  | 0.5
|  |  | M | Final refrigerant quantity |  | Was adequate refrigerant added to the system to ensure its effective operation? | Yes/No | 5 |  | 1
|  |  | M | Service gauge removal |  | Were the services gauges removed from the system and the bottle with no avoidable loss of refrigerant? | Yes/No | 5 |  | 0.3
|  |  | M | Leak test |  | Was an electronic leak test carried out during or after the charging of refrigerant? | Refer standards section 6.2 | 5 |  | 0.5
D2 | Module B - Commissioning Report | 4
|  |  | M | Ambient temperature |  | Is the ambient dry bulb temperature measured and recorded correctly on the commissioning report? |  | 5 |  | 0.2
|  |  | M | Ice tank temperature |  | Is the Ice tank temperature measured and recorded correctly on the commissioning report? | Less than -5 DegC | 5 |  | 0.2
|  |  | M | Heat recovery water tank temperature |  | Is the Heat recovery water tank temperature measured and recorded correctly on the commissioning report? | 35 DegC to 45 DegC | 5 |  | 0.2
|  |  | M | Refrigerant type |  | Is the refrigerant type recorded correctly on the commissioning report? | R134a | 5 |  | 0.2
|  |  | M | Refrigerant charge |  | Is the refrigerant charge measured and recorded correctly on the commissioning report? | 2.5-3.5 kg | 5 |  | 0.5
|  |  | M | Suction pressure |  | Is the suction pressure measured and recorded correctly on the commissioning report? | 5-20 psi / 35-140kPa | 5 |  | 0.2
|  |  | M | Evaporation temperature |  | Is the evaporation temperature determined and recorded correctly on the commissioning report? | Based on suction pressure | 3 |  | 0.3
|  |  | M | Discharge pressure |  | Is the discharge pressure measured and recorded correctly on the commissioning report? | 111 - 152psi / 770 - 1050 kPa | 5 |  | 0.2
|  |  | M | Condensing temperature |  | Is the condensing temperature determine and recorded correctly on the commissioning report? | Based on discharge pressure | 3 |  | 0.3
|  |  | M | Liquid line subcooling |  | Is the liquid line subcooling determined and recorded correctly on the commissioning report? | Condensing temp less liquid temp before TX Valve | 3 |  | 0.3
|  |  | M | Thermostatic expansion valve superheat |  | Is the Thermostatic expansion valve superheat determined and recorded correctly on the commissioning report? | 5k =/- 2K | 3 |  | 0.3
|  |  | M | Total suction superheat |  | Is the total suction superheat determined and recorded correctly on the commissioning report? | 7k =/- 2K | 3 |  | 0.3
|  |  | M | Hot gas by-pass valve setting |  | Is the Hot gas by-pass valve correctly set and recorded on the commissioning report? | 9 psi / 60kPa +/- 10% | 5 |  | 0.5
|  |  | M | Compressor operating current |  | Is the Compressor operating current measured and recorded correctly on the commissioning report? | Max 10 amps | 5 |  | 0.5
|  |  | M | Ice tank thermostat |  | Was the ice tank thermostat was correctly programmed? | Cut out -17 DegC, Cut in -10 DegC and no defrost cycle | 5 |  | 0.5
|  |  | M | Heat recovery thermostat |  | Was the heat recovery thermostat was correctly programmed? | Cut in 35 DegC, Cut out 46 DegC and no defrost cycle | 5 |  | 0.5
|  |  | M | Dual pressure control's LP settings |  | Are the dual pressure control's LP cut in and cut-out set and recorded correctly? | Cut out 4.6psi/ 46kPa Cut in 14.5psi/100kPa +/- 10% | 5 |  | 0.5
|  |  | M | Dual pressure control's HP settings |  | Is the dual pressure control's HP cut out and cut in set and recorded correctly? | Cut out 200psi/ 1380kPa Cut in 133psi/915kPa +/- 10% | 5 |  | 0.5
|  |  | M | High pressure control's settings |  | Are the high pressure control's cut in and cut out set and recorded correctly | Cut out 114psi / 785kPa, Cut in 152psi / 1050kPa +/- 5% | 5 |  | 0.5
D3 | Module B - Commissioning - Complete the Installation | 4
|  |  | M | Additional materials |  | Was the project completed without any additional materials? | Yes/No | 1 |  | 0.4
|  |  | M | Component covers |  | Were all of the components covers installed securely? | Yes/No | 1 |  | 0.4
|  |  | M | Damage to equipment |  | Were no burn marks or other damage made to any of the equipment? If Yes = 0.4 marks | Yes/No | 1 |  | 0.4
|  |  | M | System operational |  | Was the system left operating at completion of module? If Yes = 0.8 | Yes/No | 2 |  | 0.8
D4 | Module E - Commissioning Report | 3
|  |  | M | Ambient dry bulb temperature |  | Was the ambient dry bulb temperature measured and recorded correctly? | Yes/No | 5 |  | 0.2
|  |  | M | Return air dry bulb temperature |  | Was the return air dry bulb temperature measured and recorded correctly? | Yes/No | 5 |  | 0.2
|  |  | M | Supply air dry bulb temperature |  | Was the supply air dry bulb temperature measured and recorded correctly? | Yes/No | 5 |  | 0.2
|  |  | M | Indoor fan speed and mode of operation |  | Was the specified indoor fan speed and mode of operation selected and recorded correctly? | High fan speed and cooling mode | 5 |  | 0.2
|  |  | M | Refrigerant type and charge |  | Was the correct refrigerant type and refrigerant charge added to the unit and recorded correctly? | R410a and refrigerant charge (check unit specs?) | 3 |  | 0.5
|  |  | M | Suction gauge pressure |  | Was the suction pressure measured and recorded correctly? | Yes/No | 5 |  | 0.2
|  |  | M | Total suction superheat |  | Was the total suction superheat determined and recorded correctly? | Yes/No | 3 |  | 0.4
|  |  | M | Outdoor unit's current draw |  | Was the outdoor units current draw measured and recorded correctly? | Yes/No | 5 |  | 0.3
D5 | Module E - Commissioning - Complete the Installation | 3
|  |  | M | Project completed |  | Was the module completed without requiring additional materials? | Yes/No | 1 |  | 0.2
|  |  | M | Unit covers |  | Were all of the units covers installed securely? | Yes/No | 1 |  | 0.2
|  |  | M | Damage to equipment |  | Was there no damage made to the equipment? If Yes = 0.2 | Yes/No | 1 |  | 0.2
|  |  | M | System operation |  | Was the system left in operating correctly and effectively? If Yes = 1.0 | Yes/No | 2 |  | 1
Sub Criterion ID | Sub Criterion Name or Description | Day of Marking | Aspect Type M = Meas J = Judg | Aspect - Description | Judg Score | Extra Aspect Description (Meas or Judg) OR Judgement Score Description (Judg only) | Requirement (Measurement Only) | WSSS Section | Calculation Row (Export only) | Max Mark | Criterion E | Total Mark
E1 | Module C - Electrical Fault Finding | 2
|  |  | M | Supply voltage to earth |  | Was the supply voltage measured and confirmed correct? | 220v a.c +/- 10v | 5 |  | 0.5
|  |  | M | Supply voltage to neutral |  | Was the supply voltage measured and confirmed correct? | 220v a.c +/- 10v | 6 |  | 0.5
|  |  | M | Earth continuity to outdoor unit's metal frame |  | Was the earth continuity of the power supply to the outdoor unit's frame tested and found to meet requirements? | Less than 1 ohm | 6 |  | 0.5
|  |  | M | Active and Neutral continuity to the outdoor unit |  | Was the Active and Neutral continuity to the outdoor unit tested and confirmed correct? | Less than 1 ohm | 6 |  | 0.5
|  |  | M | Earth continuity to indoor unit's metal frame |  | Was the earth continuity of the power supply to the indoor unit's frame tested and found to meet requirements? | Less than 1 ohm | 6 |  | 0.5
|  |  | M | Earth continuity to the compressor |  | Was the earth continuity of the power supply to the compressor tested and found to meet requirements? | Less than 1 ohm | 6 |  | 0.5
|  |  | M | Active earth leakage |  | Was the active side of the installation tested for earth leakage using an ohm-meter prior to energising and found to be acceptable? | Infinity | 6 |  | 0.5
|  |  | M | Neutral earth leakage |  | Was the neutral side of the installation tested for earth leakage using an ohm-meter set prior to energising and found to be acceptable? | Infinity | 6 |  | 0.5
|  |  | M | Unit electrical fault |  | Was no electrical fault found during this circuit testing? If Yes = 0.5 | Yes/No | 6 |  | 0.5
|  |  | M | Compressor winding resistance testing |  | Were the resistances of the compressor's winding measured correctly and found to meet requirements? | 3.0 ohm =/- 0.2 ohm | 6 |  | 0.5
|  |  | M | Compressor winding insulation testing |  | Was the insulation resistance of the compressor's windings measured correctly and found to meet requirements? | At least 1 megohm | 6 |  | 0.5
|  |  | M | Compressor electrical fault |  | Was the compressor electrically safe to operate? | Yes/No | 6 |  | 0.5
|  |  | M | Compressor reconnection |  | Was the electrical wiring corrected re-connect to the compressor terminals? | Yes/No | 6 |  | 0.5
|  |  | M | Unit operation |  | Was the operation of the 3 components recorded correctly? | Yes/No | 6 |  | 0.5
|  |  | M | Unit's electrical fault found with in 60 minutes |  | Was the unit's electrical fault correctly identified and recorded in 60 minutes or less? | Yes/No | 6 |  | 1
|  |  | M | Unit's electrical fault found with in 45 minutes |  | Was the unit's electrical fault correctly identified and recorded in 45 minutes or less? | Yes/No | 6 |  | 1
|  |  | M | Unit's electrical fault found with in 30 minutes |  | Was the unit's electrical fault correctly identified and recorded in 30 minutes or less? | Yes/No | 6 |  | 1
|  |  | M | Units returned to original condition |  | Were the units returned to their original condition? | Yes/No | 3 |  | 0.5
Sub Criterion ID | Sub Criterion Name or Description | Day of Marking | Aspect Type M = Meas J = Judg | Aspect - Description | Judg Score | Extra Aspect Description (Meas or Judg) OR Judgement Score Description (Judg only) | Requirement (Measurement Only) | WSSS Section | Calculation Row (Export only) | Max Mark | Criterion F | Total Mark
F1 | Module D - Refrigeration Fault Finding | 2
|  |  | M | Ambient dry bulb temperature |  | Was the ambient dry bulb temperature measured and recorded correctly? | Yes/No | 5 |  | 0.5
|  |  | M | Return air dry bulb temperature |  | Was the return air dry bulb temperature measured and recorded correctly? | Yes/No | 5 |  | 0.5
|  |  | M | Supply air dry bulb temperature |  | Was the supply air dry bulb temperature measured and recorded correctly? | Yes/No | 5 |  | 0.5
|  |  | M | Indoor fan speed and mode of operation |  | Was the specified indoor fan speed and mode of operation selected and recorded correctly? | High fan speed and cooling mode | 5 |  | 0.5
|  |  | M | Refrigerant type |  | Was the correct refrigerant type identified and recorded correctly? | R410a | 3 |  | 0.5
|  |  | M | Suction pressure |  | Was the suction pressure measured and recorded correctly? | Yes/No | 6 |  | 0.5
|  |  | M | Saturated suction temperature |  | Was the saturated suction temperature determined and recorded correctly? | Yes/No | 6 |  | 0.5
|  |  | M | Discharge pressure |  | Was the discharge pressure measured and recorded correctly? | Yes/No | 6 |  | 0.5
|  |  | M | Total suction superheat |  | Was the total suction superheat determined and recorded correctly? | Yes/No | 3 |  | 0.8
|  |  | M | Compressor current draw |  | Was the compressor current draw measured and recorded correctly? | Yes/No | 6 |  | 0.5
|  |  | M | Unit's refrigeration fault found in 60 minutes or less |  | Was the unit's refrigeration fault correctly identified and recorded in 60 minutes or less? | Yes/No | 6 |  | 1
|  |  | M | Unit's refrigeration fault found in 45 minutes or less |  | Was the unit's refrigeration fault correctly identified and recorded within 45 minutes? | Yes/No | 6 |  | 1
|  |  | M | Unit's refrigeration found in 30 minutes or less |  | Was the unit's electrical fault correctly identified and recorded in 30 minutes or less? | Yes/No | 6 |  | 1
|  |  | M | Units returned to original condition |  | Were the units returned to their original condition? | Yes/No | 3 |  | 0.5
F2 | Module E - Refrigeration Fault Repair | 3
|  |  | M | Refrigeration Fault Repair |  | Was the correct fault repaired? | Yes/No | 6 |  | 1
Sub Criterion ID | Sub Criterion Name or Description | Day of Marking | Aspect Type M = Meas J = Judg | Aspect - Description | Judg Score | Extra Aspect Description (Meas or Judg) OR Judgement Score Description (Judg only) | Requirement (Measurement Only) | WSSS Section | Calculation Row (Export only) | Max Mark | Criterion G | Total Mark
G1 | Module E - Reclaim Refrigerant | 3
|  |  | M | Electrical supply isolation |  | Was the power supply to air conditioner isolated before refrigerant recovery commenced? | Yes/No | 6 |  | 0.15
|  |  | M | Manifold gauge fitting |  | Were the service manifold gauge lines fitted to the system correctly with minimal loss of refrigerant? | Yes/No | 6 |  | 0.15
|  |  | M | Refrigerant cylinder selection |  | Was the correct refrigerant recovery cylinder selected and used? | Yes/No | 6 |  | 0.2
|  |  | M | Refrigerant cylinder weight |  | Was the refrigerant recovery cylinder weighed and recorded correctly before recovery started? | Yes/No | 6 |  | 0.2
|  |  | M | Recovery system connections |  | Were the refrigerant recovery cylinder, machine and lines connected correctly the first time with minimal loss of refrigerant? | Yes/No | 6 |  | 0.2
|  |  | M | Refrigerant recovery |  | Was the full refrigerant charge recovered from the system using recovery equipment? | Yes/No | 6 |  | 0.4
|  |  | M | Refrigerant leak test |  | Was an electronic leak detector used to check for leaks during recovery of refrigerant? | Yes/No | 6 |  | 0.15
|  |  | M | System pressure |  | Was the system pressure/s at atmospheric pressure or just below (0psi to -5psi/0Kpa to -35kPa) after recovery was completed? | Yes/No | 6 |  | 0.15
|  |  | M | Disconnection of recovery equipment |  | Was the recovery equipment disconnected with minimal loss of refrigerant and all service caps fitted? | Yes/No | 6 |  | 0.15
|  |  | M | Recovered refrigerant quantity |  | Was the quantity of refrigerant recovered from the system correctly recorded? | Yes/No | 6 |  | 0.15
G2 | Module E - Pressure Test | 3
|  |  | M | Test pressure |  | Did the test pressure during all attempts meet required standards and specifications? | Refer standards section 4 and test project 55 DegC = 3,339 kPa +/- 35 kPa or 484 PSI +/- 5 PSI | 4 |  | 0.15
|  |  | M | System valves |  | Were all the appropriate valves opened to ensure pressure testing of the entire system? | Check all valves in system | 4 |  | 0.15
|  |  | M | Gauges fitted |  | Were the gauges and gauge lines correctly fitted to the system? | Refer standards section 4 | 4 |  | 0.15
|  |  | M | Dry Nitrogen |  | Was dry Nitrogen safely added to the system to the required test pressure? | Refer standards section 4 and test project instructions | 4 |  | 0.15
|  |  | M | Leak test |  | Was the system leak tested while under pressure? | Soapy water solution, Refer standards section 4 | 4 |  | 0.3
|  |  | M | First leak test |  | Were no leaks were detected on FIRST pressure test attempt? | Test project instructions | 4 |  | 0.4
|  |  | M | Final leak test |  | Did the system hold the test pressure for required standing time (15 minutes) after any leaks repaired? | Refer standards section 4, and test project | 4 |  | 1
|  |  | M | Pressure release |  | Was the dry Nitrogen safely released from system at completion of pressure test? | Refer standards section 4 | 4 |  | 0.15
G3 | Module E - Evacuation | 3
|  |  | M | System valves |  | Were the appropriate valves opened to ensure evacuation of the entire system? | Yes/No | 4 |  | 0.15
|  |  | M | Vacuum pump |  | Was the vacuum pump connected to the system correctly? | Yes/No | 4 |  | 0.15
|  |  | M | Vacuum gauge |  | Was the vacuum gauge installed so it could be isolated from the vacuum pump and still measure the system's pressure? | Yes/No | 4 |  | 0.15
|  |  | M | Vacuum pressure reached |  | Did the system reach the required vacuum level on the first attempt? | At least 1000 microns | 4 |  | 0.4
|  |  | M | Vacuum holding pressure |  | Did the vacuum hold when isolated from the vacuum pump for 10 minutes after the FIRST attempt? | Refer standards section 4 and test project. Not rise more than 500 microns in 10 minutes | 4 |  | 0.4
|  |  | M | Final vacuum pressures |  | Did the system reach and hold the required vacuum on the FINAL attempt? | Refer standards section 4, - and test project | 4 |  | 1
G4 | Module E - Charge with Refrigerant | 3
|  |  | M | Refrigerant service manifold |  | Was the refrigerant service manifold correctly connected to the refrigeration system and refrigerant cylinder to charge the system with refrigerant? | Yes/No | 5 |  | 0.15
|  |  | M | Refrigeration system's valves |  | Were all the refrigeration system's valves in correct position to charge the system with refrigerant? | Yes/No | 5 |  | 0.15
|  |  | M | Liquid refrigerant |  | Was liquid refrigerant added to the liquid line only (not suction)? | Yes/No | 5 |  | 0.15
|  |  | M | Adding liquid refrigerant |  | Was liquid refrigerant added to the system using correct method with no or minimal loss of refrigerant to the atmosphere? | R410a liquid charge | 5 |  | 0.15
|  |  | M | Liquid refrigerant quantity |  | Was the correct quantity of refrigerant added to the system as specified | ?kg +/- 10g | 5 |  | 1
|  |  | M | Service gauge removal |  | Were the services gauges removed from the system and the bottle with no avoidable loss of refrigerant? | Yes/No | 5 |  | 0.15
|  |  | M | Leak test |  | Was an electronic leak test carried out after the charging of refrigerant? | Refer standards section 6.2 | 5 |  | 0.15
Sub Criterion ID | Sub Criterion Name or Description | Day of Marking | Aspect Type M = Meas J = Judg | Aspect - Description | Judg Score | Extra Aspect Description (Meas or Judg) OR Judgement Score Description (Judg only) | Requirement (Measurement Only) | WSSS Section | Calculation Row (Export only) | Max Mark | Criterion H | Total Mark
H1 | Module A - Work Practices and Safety | 1
|  |  | M | Protective gloves |  | Were Protective gloves were worn at all times when exposed to heat sources? (armed covered) | Yes/No | 1 |  | 0.25
|  |  | M | Protective eye wear |  | Were protective eye wear was worn at all times while brazing? | Yes/No | 1 |  | 0.25
|  |  | M | Tools and safe work practices |  | Did the competitor always use the correct tool and safe work practices for every activity? | Yes/No | 1 |  | 0.25
|  |  | M | Brazing torches and regulators |  | Were the competitors brazing torches and regulators are left at atmospheric pressure on completion of module? | Yes/No | 1 |  | 0.25
H2 | Module B - Work Practices and Safety | 4
|  |  | M | Protective gloves |  | Were Protective gloves were worn at all times when exposed to heat sources? (armed covered) | Yes/No | 1 |  | 0.5
|  |  | M | Protective eye wear |  | Were protective eye wear was worn at all times while brazing? | Yes/No | 1 |  | 0.5
|  |  | M | Tools and safe work practices |  | Did the competitor always use the correct tool and safe work practices for every activity? | Yes/No | 1 |  | 0.5
|  |  | M | Brazing torches and regulators |  | Were the competitors brazing torches and regulators are left at atmospheric pressure on completion of module? | Yes/No | 1 |  | 0.5
H3 | Module C - Work Practices and Safety | 2
|  |  | M | Protective gloves |  | Were Protective gloves were worn at all times when exposed to heat sources? (armed covered) | Yes/No | 1 |  | 0.5
|  |  | M | Protective eye wear |  | Were protective eye wear was worn at all times while brazing? | Yes/No | 1 |  | 0.5
|  |  | M | Tool and safe work practices |  | Did the competitor always use the correct tool and safe work practices for every activity? | Yes/No | 1 |  | 0.25
|  |  | M | Tool and equipment safety |  | Were the competitors tools and equipment in a safe condition on completion of module? | Yes/No | 1 |  | 0.25
H4 | Module D - Work Practices and Safety | 2
|  |  | M | Protective gloves |  | Were Protective gloves were worn at all times when exposed to heat sources? (armed covered) | Yes/No | 1 |  | 0.35
|  |  | M | Protective eye wear |  | Were protective eye wear was worn at all times while brazing? | Yes/No | 1 |  | 0.35
|  |  | M | Tool and safe work practices |  | Did the competitor always use the correct tool and safe work practices for every activity? | Yes/No | 1 |  | 0.25
|  |  | M | Tool and equipment safety |  | Were the competitors tools and equipment in a safe condition on completion of module? | Yes/No | 1 |  | 0.25
H5 | Module E - Work Practices and Safety | 3
|  |  | M | Protective gloves |  | Were Protective gloves were worn at all times when exposed to heat sources? (armed covered) | Yes/No | 1 |  | 0.35
|  |  | M | Protective eye wear |  | Were protective eye wear was worn at all times while brazing? | Yes/No | 1 |  | 0.35
|  |  | M | Tool and safe work practices |  | Did the competitor always use the correct tool and safe work practices for every activity? | Yes/No | 1 |  | 0.25
|  |  | M | Tool and equipment safety |  | Were the competitors tools and equipment in a safe condition on completion of module? | Yes/No | 1 |  | 0.25
Sub Criterion ID | Sub Criterion Name or Description | Day of Marking | Aspect Type M = Meas J = Judg | Aspect - Description | Judg Score | Extra Aspect Description (Meas or Judg) OR Judgement Score Description (Judg only) | Requirement (Measurement Only) | WSSS Section | Calculation Row (Export only) | Max Mark | Criterion I | Total Mark
[11 empty] | Competition | Total Mark